## Slide 1: Translation (XSLT) Data and Model
Distribution Modeling in Modelica
Faster, More Flexible Analysis
Notes: I recently attended the American Modelica Conference 2020 to survey the possibility of using Modelica for distribution planning. I’ve been using DNV’s distribution modeling software for the last five years and it lacked fast and flexible analysis. One of my jobs at City Utilities in Springfield, Missouri is system planner. Our system is predominantly municipal and has 117,000 electrical meters. While we attract businesses because of our low electric costs, our engineering group like much of the industry, is young, inexperienced and focuses on system expansion. I only get to spend about 25 percent of my time on planning and I have two that can spend part of their time creating planning products.

## Slide 2: Academic/Software View Glen K. Halley, P.E.
Physical Design – Civil Work
  Transmission – PLS Cadd
  Distribution – PLS Cadd Lite
  Substation - Substation Design Suite (SDS), Physical
Electrical Design – Electrical Work
  Distribution – DNV Synergi Electric
  Substation – SDS Protection & Control
Operations
  Duty Supervisor
  Storm Operations Scheduler
  Load Analysis for Switching Plans
Information Systems
  Mapping – ESRI, Geographic Information Systems (GIS)
  Automatic Meter Reading (AMR) - Itron
Notes: We are short of engineer resources where I work, and software is the key to resolving these constraints.
Training people to use software is the most important roadblock. Intuitive software is key. Seemingly diversionary work such as exporting GIS data to Synergi moves to the top of the list. Electrical Engineers instinctively understand a model of a statically loaded power system especially if you’re looking at a small area. This requires minimal data. Planning requires consolidating more data, more rapidly than in the past, with better characterizations.

## Slide 3: Modelica Distribution Planning Case and Implementation
Introduction
  Planning Products
  Distribution Process
  Problems to Solve
Transmission CIM to Modelica
  Transparent, Accountable, Certifiable, and Fast like OpenIPSL
  Process Overview
Extra Hurdles for Distribution

## Slide 4: Year of Distribution Planning
New Loads
  Three greater than 25 percent of feeder capacity
  One greater than 25 percent of transformer capacity
  Average feeder is 50 percent loaded
  Remedy if feeder is greater than 75 percent loaded from switching to building new substations.
Maintenance Outages
  Twenty-five planned
  Three unplanned
Notes: We work in steps. First, feeder capacity; then transformer capacity. We use tools such as transferring load first followed by wire upgrades followed by transformer upgrades.

## Slide 5: Year of Distribution Planning (cont’d)
Economic Development
  Tens questions about capacity
Advanced Analysis
  Motor Starts
  Automatic Transfer
  Voltage Compliance
  Harmonics
  Distributed Energy Resources (DER)

## Slide 6: Mise En Place Modeling Process “everything in its place”
Use Modelica and OpenIPSL to Model
  Transparent
  Accountable
  Certifiable
  Fast
Create loads that are:
  Aggregated on key constraints: temperature, time-of-day, and VARs.
  Individually based on best model (ie residential has gas and heat-pump)
  Incorporates state variables such as AMR

## Slide 7: Transmission/Distribution Equipment Import
Distribution
  GIS
  Common Information Model (CIM)
  CIM Entsoe defined
Transmission
  PSS/E or other
  CIM Entsoe defined
  Hand-built
Equipment/ State
Characterized
Load
Modelica
Model
Notes: The first step in creating a validated model is transferring the equipment and equipment state. For distribution systems the information comes from GIS. For transmission systems, PSS/E can be a source among others. The common information model (CIM) is used for data exchange. Many sources are actively creating CIM exports. Therefore, I think CIM to Modelica translation provides the equipment and state data. The CIM Entsoe translation is really a one-for-one translation because of OpenIPSL. For distribution, GIS CIM to Modelica is easy. The hard part would be to create validated components that would closely match the GIS CIM data export.

## Slide 8: XSLT to translate CIM to MO
Common Information Model (CIM) from Siemens PTI PSS®ODMS
  Readable by Machine not Humans (XML)
  Normalized – common data used in multiple types is linked using keys
  Multiple CIM Files including
    State Variables (SV)
    Dynamic (DY)
    Equipment (EQ)
    Topology (TP)
    Steady-state Hypothesis (SSH)
Modelica
  Components for Standard Models: Bus, Line, Load, Generation, Fault, Xfmr

## Slide 9: Rapidly Translate CIM to Modelica eXtensible Stylesheet Language (XSLT)
XSLT Engine can run in .NET, Java, Python, and on-line
Creating XSLT file is the key
Equipment/State CIM file
Modelica
MO file
XSLT
Engine
Translation XSLT file
Notes: The roadblock for using these Modelica chunks is creating and validating the models. For transmission, Luigi and Marcello validate the model with OpenIPSL. I have used extensible stylesheet language (XSLT) for CIM translation. CIM is clearly defined by Entsoe’s models. While I haven’t looked at CIM for distribution, the most prevalent source will be GIS. Therefore, CIM exports from GIS will be used to determine the chunks used to create Modelica components.

## Slide 10: Translate PSS/E CIM to Modelica with XSLT
CIM File
<cim:BusbarSection rdf:ID="_70393951-9562-11e7-9e89-b46d83638f70">
<cim:Equipment.EquipmentContainer rdf:resource="#_7039395a-9562…" />
<cim:IdentifiedObject.name>BUS1</cim:IdentifiedObject.name>
</cim:BusbarSection>
<cim:BusbarSection rdf:ID="_7039396c-9562-11e7-9e89-b46d83638f70">
<cim:Equipment.EquipmentContainer rdf:resource="#_70393975-9562-…" />
<cim:IdentifiedObject.name>BUS2</cim:IdentifiedObject.name>
</cim:BusbarSection>
…
XSLT File
<xsl:template match="/rdf:RDF">
<xsl:text>model CIM16_IEEE_9bus “auto-g."
</xsl:text>
<xsl:for-each select="cim:BusbarSection">
<xsl:text>OpenIPSL.Electrical.Buses.Bus </xsl:text>
<xsl:value-of select="cim:IdentifiedObject.name"/>
<xsl:text> "auto-g." annotation(Placement(transformation(extent = {{30, -40}, {50, -20}})));
</xsl:text>
</xsl:for-each>
…
XSLT Engine
Modelica
model CIM16_IEEE_9bus "auto-g."
OpenIPSL.Electrical.Buses.Bus BUS1 "auto-g." annotation(Placement(transformation(extent = {{30, -40}, {50, -20}})));
OpenIPSL.Electrical.Buses.Bus BUS2 "auto-g." annotation(Placement(transformation(extent = {{30, -40}, {50, -20}})));
Notes: I think the translation is transparent and accountable because the code is short and direct. For example, the bus translation

## Slide 11: XSLT’s use for Distribution Modeling
XSLT maps GIS asset types to a separate file of electrical properties
  Line instances = component * length
XSLT Aggregation algorithms simplify the model for certain analysis
  Voltage: Switches could be removed, and lines combined
System state algorithms using correlation analysis with:
  Phasor Measurement Units (PMUs) from SEL Relays
  AMR and EMS data
Notes: XSL

## Slide 12: Summary
Transmission Modeling with Modelica can be flexible and fast with CIM translation and OpenIPSL
CIM translation can be transparent and accountable like OpenIPSL
Widespread Distribution Modeling Using Modelica Requires:
  Modelica components created from GIS CIM exports
  Rapid and automated load characterization
  Additional algorithms

## Slide 13: Contact Information
Glen K. Halley, P.E.
Glen@GKHSoftware.com
Glen Halley | LinkedIn